## Controls Table
LEGEND: | Link to resource | Controls Table for Compressed Gases, Cryogenic Liquids, Other (companion to Fixed Gas Detection (FGD) Determination Process for Compressed Gases, Cryogenic Liquids, Other)
Review comment in upper right corner for more information
*Retain Controls Table with applicable columns with HACF. Instructions are provided in the second tab at the bottom titled 'Excel Instructions'.
| Control | Compressed Gas Cylinder connected to equipment | Cryogenic Liquid Dewar or Cylinder connected to equipment | Cryogenic Liquid Dewar for Storage or Short-term Use not connected to equipment | Cryogenic Liquid Dewar Dispensing Activities | For Other all controls are for consideration and only required if applicable to operations, with exception to where required by Code. | Other Specialty Operations | Other Facility Operations | Other Underground Parkades | Controls documentation to supplement HACF • Include date implemented • If a required control can not be implemented, provide justification and contact EHS
Required Engineering (ENG) Controls | Activity is conducted in an appropriate space/location (i.e. a designated lab/workshop in Chematix or can submit Work Request to have space assessed for intended purpose). As per the Alberta Fire Code, some volatile chemicals are not permitted below grade - submit Work Request to engage Campus Architecture if unsure. | ü | ü | ü | ü |  | ü
| Installation by competent personnel of appropriate lines, tubing, conduit, etc. in a manner to minimize accidental contact or impact - if competent personnel not available, submit Work Request as per note for installation resource. | ü | ü |  |  |  | ü | ü
| If HVAC is down for the space, activities using compressed gases will not be conducted. | ü |  |  |  |  | ü | ü
| If HVAC is down for the space, activities using cryogenic liquids will not be conducted. |  | ü | ü | ü |  | ü | ü
| If HVAC is down for the space, activities with potential to create a hazardous atmosphere will not be conducted. | [5 empty] | ü | ü
| Fixed Gas Detection (as required by Code or UCalgary) - submit Work Request to engage Life Safety. |  |  |  | ü (UCalgary req'd) |  |  | ü (Code req'd) | ü (Code req'd)
| Dedicated Local Exhaust Ventilation (as required by Code or UCalgary) - submit Work Request to engage Campus Engineering. |  |  |  | ü (UCalgary req'd) |  |  | ü (Code req'd) | ü (Code req'd)
| Ventilated enclosures (e.g. gas cabinet) are required for some compressed gas types - refer to the Chemical and Laboratory Safety - Compressed Gas Cylinder Standard for more information. | ü |  |  |  |  | ü | ü
Required Administrative (ADM) Controls | Completion of regular leak testing - frequency to be included in SOP for this activity (refer to the Chemical and Laboratory Safety - Compressed Gas Cylinder Standard for how to conduct leak testing). | ü | ü |  |  |  | ü | ü
| Completion of regular safety checks of dewar - frequency to be included in SOP for this activity (refer to Chemical and Laboratory Safety - Cryogenic Materials Standard Supplemental Information for how to conduct safety checks). |  | ü | ü | ü |  | ü
| Review and adherence to manufacturers Operation Manuals for cylinders and equipment using compressed gases. | ü |  |  |  |  | ü | ü
| Review and adherence to manufacturers Operation Manuals for dewars and equipment using cryogenic liquids. |  | ü | ü | ü |  | ü | ü
| Review and adherence to manufacturers Operation Manual for NMR (e.g. Site Planning Guide for NMR). |  |  |  | ü |  | ü
| Review and adherence to manufacturers Operation Manuals for operations and equipment with potential to create a hazardous atmospheres. | [5 empty] | ü | ü
| Review and adherence to the Chemical and Laboratory Safety - Compressed Gas Cylinder Standard. | ü |  |  |  |  | ü | ü
| Review and adherence to the Chemical and Laboratory Safety - Cryogenic Materials Standard Supplemental Information. |  | ü | ü | ü |  | ü | ü
| Review and adherence to applicable Laboratory Safety Manual documentation including operational considerations for after hours work, working alone, and unattended operations. | ü | ü | ü | ü |  | ü | ü
| Development and implementation of written Safe Operating Procedures (e.g. Chemical and Laboratory Safety - SOP template) for operations. | ü | ü | ü | ü |  | ü | ü
| Retain training records for those conducting operations (e.g. leak tests, filling, etc.). | ü | ü | ü | ü |  | ü | ü
| Adding the following to the Operational Requirements - Lab Placard special hazards section: Cryogenic Materials. |  | ü | ü | ü |  | ü
| Reporting to EHS if a situation occurs where alarms were activated and/or leaks into the space were noted. | ü | ü | ü | ü |  | ü | ü | ü
Engineering (ENG) Controls to Consider | Fixed Gas Detection - submit Work Request to engage Life Safety. | ü | ü |  |  |  | ü
| Portable/personal monitors - can review Standards - Personal Gas Monitor Standard for guidance. | ü | ü |  | ü |  | ü | ü
| Dedicated Local Exhaust Ventilation - submit Work Request to engage Campus Engineering. | ü | ü |  |  |  | ü
| Minimum quantity purchased to meet needs, and/or as per the Chemical and Laboratory Safety - Compressed Gas Cylinder Standard. | ü | ü | ü | ü |  | ü | ü
MUST NOT exceed Alberta Fire Code maximum allowable - submit Work Request to engage Campus Architecture if unsure. Alberta Fire Code maximum allowable should not be used to justify purchasing more than is necessary.
| Ventilated enclosure (e.g. gas cabinet) - refer to the Chemical and Laboratory Safety - Compressed Gas Cylinder Standard for more information. | ü |  |  |  |  | ü
Note on E5: For example: sample storage dewar; large dewar used to transfer to smaller dewar. Transfer refers to decanting or topping up activities; no FGD required.
Note on F5: For example: dispensing as part of a permanent/active localized activity; high frequency dispensing by designated personnel in locations with FGD such as Stores or NMRs.
Note on H5: For example: does not fit into another column but controls and/or FGD are appropriate for activities.
Note on I5: For example: Olympic Oval; Heating Plant; Mechanical Room chillers; Gas Storage Room. Gas Storage Room refers to a room that is designed and intended for gas cylinder storage.
Note on B7: For requesting an Internal Resource direct to: Faculty of Science Glass Blowing Mark Toonen, Glassblower For requesting an External Resource direct to: Campus Engineering
Note on B8: Indications HVAC may be down: quieter; air feels warmer and/or more stale; Facilities Customer Care notification; can add 'ribbbon' to supply vent to verify movement. It is recognized that there may be extenuating circumstances where this cannot be achieved; however, best efforts to meet this requirement are mandatory.
Note on B9: Indications HVAC may be down: quieter; air feels warmer and/or more stale; Facilities Customer Care notification; can add 'ribbbon' to supply vent to verify movement. It is recognized that there may be extenuating circumstances where this cannot be achieved; however, best efforts to meet this requirement are mandatory.
Note on B10: Indications HVAC may be down: quieter; air feels warmer and/or more stale; Facilities Customer Care notification; can add 'ribbbon' to supply vent to verify movement. It is recognized that there may be extenuating circumstances where this cannot be achieved; however, best efforts to meet this requirement are mandatory.
Note on F11: Required due to typically large volume, tend to be in small spaces, known existing have FGD installed, thought to be limited activity, potential for hazard if dispensing not done correctly.
Note on I11: References for Ammonia at OO: NFPA1, NFPA 72, NFPA 715, ASHRAE 15, IIAR 2A- International Institute of Ammonia Refrigeration References for Chillers at HP & Mechanical Rooms: CSA B52:18 Mechanical refrigeration code.
Note on J11: References for Ammonia at OO: NFPA1, NFPA 72, NFPA 715, ASHRAE 15, IIAR 2A- International Institute of Ammonia Refrigeration References for Chillers at HP & Mechanical Rooms: CSA B52:18 Mechanical refrigeration code.
Note on F12: Required due to typically large volume, tend to be in small spaces, known existing have FGD installed, thought to be limited activity, potential for hazard if dispensing not done correctly.
Note on I12: References for Ammonia at OO: NFPA1, NFPA 72, NFPA 715, ASHRAE 15, IIAR 2A- International Institute of Ammonia Refrigeration References for Chillers at HP & Mechanical Rooms: CSA B52:18 Mechanical refrigeration code.
Note on J12: References for Ammonia at OO: NFPA1, NFPA 72, NFPA 715, ASHRAE 15, IIAR 2A- International Institute of Ammonia Refrigeration References for Chillers at HP & Mechanical Rooms: CSA B52:18 Mechanical refrigeration code.
Issued by: Environment, Health and Safety
Issue Date: March 2022 Revision #: 1 Revision Date: Oct 2022

## Excel Instructions
Navigating in Excel
Instructions | Sceen Captures
Hide/Expand Columns
To hide and expand individual and or multiple columns, see below steps.
1. To hide a single column, right click on the column letter at the top of the spreadsheet.
2. Select 'Hide' from the pop up menu.
3. To hide multiple columns, click on the first column and drag across the columns you wish to hide.
4. Select 'Hide' from the pop up menu.
Note: To 'Unhide' a column/columns, right click on the column letter(s) and select 'Unhide' from the pop up menu.
2. Filter Data
To focus on a specific set of data, see below steps on how to filter cells.
1. Click on the column letter at the top of the spreadsheet.
2. On the 'Home' tab, click 'Sort & Filter'.
3. Click 'Filter'. A drop-down arrow will now be displayed at the top of the column.
3. Print Selection
To print a data selection, worksheet or workbook see below steps.
1. On the worksheet, click and drag to select the cells you want to print.
2. Click File
3. Click 'Print'.
4. Navigate to 'Settings' and select the 'Print Selection' drop down. To print only the selected area, click 'Only print the current selection'. To print a worksheet, select 'Print Active Sheets' or to print the workbook, select 'Print Entire Workbook'.
5. Once selected, a preview of the print will appear, ensure the section you wish to print appears before clicking 'Print'.